## Instructions
Instructions Sheet
PWD Water Service Line Sizing Model
Submitted Date:
Contact Name:
Submitting Firm:
Contact Email:
Contact Phone:
Project Address:
Project Name & Specifc Connection:
Instructions Page:
Step 1: Fill out project information above.
Page 1:
Step 2: Select proposed water service line size.
Step 3: Select the type of predominant supply systems (flush tanks or flushometer valves).
Step 4: Enter the total number of fixtures for each fixture type as applicable. The total number of fixtures should include all the existing fixtures to remain and proposed fixtures to be added if the project is part of the building addition/ renovation/ alteration. The domestic demand is computed based on the total WSFU* and type of predominate supply systems.
Page 2:
Step 5: Enter the total lawn sprinkler, total continuous mechanical, and total intermittent mechanical demands, as applicable.
Step 6: If a booster pump is proposed, enter the pump design and pump maximum demands.
Step 7: If the proposed service connection is combined (fire + domestic), enter fire demands, as applicable.
Page 3:
Step 8: Enter the hydrant flow test results.
Step 9: Enter the design pressure at the main used in the design calculations.
Step 10: Enter the supply main and highest fixture elevation to compute static head loss.
Step 11: Enter the pipe length between the supply main and the building, the proposed pipe size, C value, and other pipe losses for the domestic connection to calculate total pipe losses between the supply main and the building.
Step 12: Enter the pressure losses due to meter, backflow prevention assembly, and special fixture, as applicable. Enter the pipe losses inside the building. Enter the pressure gain (if any) due to pumps. Minimum pressure required for most fixtures by the Philadelphia Plumbing Code is 20 psi.

## 1-Demand Worksheet
Demand Calculation Worksheet
PWD Water Service Line Sizing Model
Proposed Service Line Size |  |  | 3/4-Inch |  | Predominate Supply Type |  |  |  | Flush Tanks
Fixture Type | Occupancy |  | Type of Supply Control |  |  | No. of Fixtures | X | Load Value |  |  | Water Service Fixture Unit Total
=
Full-bath group | Private |  | Flush Tank |  |  | 0 | X | 3.6 |  | = | 0 | #REF!
Full-bath group | Private |  | Flushometer Valve |  |  | 0 | X | 8 |  | = | 0 | #REF!
Bathtub | Private |  | Faucet |  |  | 0 | X | 1.4 |  | = | 0 | #REF!
Bathtub | Public |  | Faucet |  |  | 0 | X | 4 |  | = | 0 | #REF!
Dishwasher | Private |  | Automatic |  |  | 0 | X | 1.4 |  | = | 0 | #REF!
Drinking Fountain | Public |  | 3/8" Valve |  |  | 0 | X | 0.25 |  | = | 0 | #REF!
Kitchen Sink | Private |  | Faucet |  |  | 0 | X | 1.4 |  | = | 0 | #REF!
Kitchen Sink | Commercial |  | Faucet |  |  | 0 | X | 4 |  | = | 0 | #REF!
Lavatory Sink | Private |  | Faucet |  |  | 0 | X | 0.7 |  | = | 0 | #REF!
Lavatory Sink | Public |  | Faucet |  |  | 0 | X | 2 |  | = | 0 | #REF!
Service Sink (incl. Mop Sink) | Commercial |  | Faucet |  |  | 0 | X | 3 |  | = | 0 | #REF!
Shower Head | Private |  | Mixing Valve |  |  | 0 | X | 1.4 |  | = | 0 | #REF!
Shower Head | Public |  | Mixing Valve |  |  | 0 | X | 4 |  | = | 0 | #REF!
Urinal | Public |  | 1" Flushometer |  |  | 0 | X | 10 |  | = | 0 | #REF!
Urinal | Public |  | 3/4" Flushometer |  |  | 0 | X | 5 |  | = | 0 | #REF!
Urinal | Public |  | Flush Tank |  |  | 0 | X | 3 |  | = | 0 | #REF!
Washing Mach. (8 lb.) | Private |  | Automatic |  |  | 0 | X | 1.4 |  | = | 0 | #REF!
Washing Mach. (8 lb.) | Public |  | Automatic |  |  | 0 | X | 3 |  | = | 0 | #REF!
Washing Mach. (15 lb.) | Public |  | Automatic |  |  | 0 | X | 4 |  | = | 0 | #REF!
Water Closet | Private |  | Flushometer Valve |  |  | 0 | X | 6 |  | = | 0 | #REF!
Water Closet | Private |  | Flush Tank |  |  | 0 | X | 2.2 |  | = | 0 | #REF!
Water Closet | Public |  | Flushometer Valve |  |  | 0 | X | 10 |  | = | 0 | #REF!
Water Closet | Public |  | Flush Tank |  |  | 0 | X | 5 |  | = | 0 | #REF!
Water Closet | Any |  | Flushometer Valve |  |  | 0 | X | 2 |  | = | 0 | #REF!
Hose Bibb 5/8" | Any |  | Valve |  |  | 0 | X | 2.5 |  | = | 0 | #REF!
Hose Bibb 3/4" | Any |  | Valve |  |  | 0 | X | 5 |  | = | 0 | #REF!
Other | [5 empty] | 0 | X |  |  | = | 0 | #REF!
Other | [5 empty] | 0 | X |  |  | = | 0 | #REF!
Notes: 1If the total WSFU is greater than 5000, this spreadsheet can not be used in calculating domestic demand. Provide an alternate method for computing the peak demand. |  |  |  | Total WSFUs1 |  |  |  |  | 0 |  |  | units
|  |  |  | Total Calculated Demand (gpm) |  |  |  |  | 0 |  |  | gpm

## 2-Meter Size Worksheet
Meter Sizing Worksheet
PWD Water Service Line Sizing Model
Proposed Service Line Size |  |  | 3/4-Inch
Demand from WSFU Calculation, gpm |  |  | 0
Mechanical Considerations (all if applicable) |  |  | Demand, gpm
Continuous Mechanical Demand |  |  | 0
Intermittent Mechanical Demand |  |  | 0
Lawn Sprinkler Demand |  |  | 0
Booster Pump Additional Demand1 |  |  | 0
Total Fixture + Mechanical + Irrigation Demand |  |  | 0
Fire Considerations (for RFSS Combined Systems)
Total Fire Demand (per NFPA requirements) |  |  | 0
Fire Pump Flow Rating |  |  | 0
Totals Fire Demand |  |  | 0
Total Peak Demand, gpm |  |  | 0
Domestic Meter Sizing Summary
Will Proposed Meter Size Accurately Measure Peak Flows? |  |  | Yes
Is Calculated Peak Flow less than or equal to Allowable Continuous Flow Rate through Meter? |  |  | No
Notes:
1Fire Consideration Totals to be the difference between peak fixture demand (Tab 1) and added fire considerations; if fire demand totals are less than peak fixture demand, these values are 0. Domestic fixtures are assumed 'off' during fire events.
2Service line to be of same size as meter from tap through backflow preventer.

## 3-Pressure Worksheet
Available Pressure Worksheet
PWD Water Service Line Sizing Model
Hydrant Flow Test Results1
Date of Test:
Static Pressure, psi.
Residual Pressure, psi.
Design Pressure at the Main |  |  | 0 | psi.
Supply Main Elevation, ft. |  |  | 0 | ft.
Highest Fixture Elevation, ft. |  |  | 0 | ft.
Pressure Change due to Elevation |  |  | 0 | psi.
Total Pipe Losses
Main to Building Pipe Lenth, ft. |  |  | 0
Peak Demand, gpm |  |  | 0
Pipe Size, inch |  |  | 0
C Value2 |  |  | 0
Pipe Friction Losses to Building, psi.3 |  |  | 0
Other Losses to Building (if any), psi. | Additional Losses |  | 0
Total Losses to Building, psi |  |  | 0
Available Pressure at Building, psi. | Additional Losses |  | 0
V (fps) 4 |  |  | 0
Available Pressure at Highest Fixture
Design Pressure at the Main, psi. |  |  | 0
Total Losses to Building, psi |  |  | 0
Static Head Pressure Change, psi. |  |  | 0
Meter Loss, psi. |  |  | 0
Backflow Prevention Loss, psi. |  |  | 0
Pipe Losses Inside the Building, psi.5,6 | Additional Losses |  | 0
Special Fixture or Other Loss, psi. | Additional Losses |  | 0
Pressure Gain due to Booster Pump, psi. |  |  | 0
Maximum Pressure Available at Highest Fixture, psi.7 |  |  | 0
Notes:
1Provide hydrant test results, signed by PWD Representative.
2Average C value for commnly used copper is 135. Ductile iron average is 140.
3Pipe friction losses to building calculated using Hazen–Williams equation.
4The maxumum reccomended flow velocity is 15 fps for ductile iron pipe
5Values should be provided by design engineer licensed in Pennsylvania. Supporting documentation should be attached with application.
6Pipe losses within the building to consider from building entry to most hydraulically remote fixture.
7Minimum pressure required
for most fixtures per Philadelphia Plumbing Code is 20 psi.
8All values to be entered as positive.

## 4-Demand Interpolation Graph
Demand Interpolation Sheet
PWD Water Service Line Sizing Model
Total WSFUs |  |  | 0 | 0
Domestic Demand, gpm |  |  | 0
Predominate Supply Systems |  |  | Flush Tanks

## Demand Interpolation (hidden) (hidden)
|  |  | Values for Demand Interpolation | [5 empty] | Drop Down Menus
|  |  | Philadelphia Service Line Sizing Permitting |  |  | Demand Calculation |  |  | Service Line Sizes | Predominate Supply Types
|  |  | From PPC Appendix-E |  |  | Flush Tanks |  |  | 3/4-Inch | Flush Tanks
[6 empty] | y = -2E-05x2 + 0.1896x + 18.404 |  |  | 1-Inch | Flushometer Valves
[6 empty] | WSFU= | 0 | Units | 1.5-Inch
| FLUSH TANKS |  |  | FLUSHOMETER TANKS |  | DEMAND= | 18.4042 | gpm | 2-Inch
| WSFU | GPM |  | WSFU | GPM | y= -1E-05x2 + 0.1813x + 34.163 |  |  | 3-Inch
| 1 | 3 |  | 1 | - | Flushometers |  |  | 4-Inch
| 2 | 5 |  | 2 | - | WSFU= | 0 | Units | 6-Inch
| 3 | 6.5 |  | 3 | - | DEMAND= | 34.163 | gpm | 8-Inch
| 4 | 8 |  | 4 | - |  |  |  | 10-Inch
| 5 | 9.4 |  | 5 | 15
| 6 | 10.7 |  | 6 | 17.4
| 7 | 11.8 |  | 7 | 19.8
| 8 | 12.8 |  | 8 | 22.2
| 9 | 13.7 |  | 9 | 24.6
| 10 | 14.6 |  | 10 | 27
| 11 | 15.4 |  | 11 | 27.8
| 12 | 16 |  | 12 | 28.6
| 13 | 16.5 |  | 13 | 29.4
| 14 | 17 |  | 14 | 30.2
| 15 | 17.5 |  | 15 | 31
| 16 | 18 |  | 16 | 31.8
| 17 | 18.4 |  | 17 | 32.6
| 18 | 18.8 |  | 18 | 33.4
| 19 | 19.2 |  | 19 | 34.2
| 20 | 19.6 |  | 20 | 35
| 25 | 21.5 |  | 25 | 38
| 30 | 23.3 |  | 30 | 42
| 35 | 24.9 |  | 35 | 44
| 40 | 26.3 |  | 40 | 46
| 45 | 27.7 |  | 45 | 48
| 50 | 29.1 |  | 50 | 50
| 60 | 32 |  | 60 | 54
| 70 | 35 |  | 70 | 58
| 80 | 38 |  | 80 | 61.2
| 90 | 41 |  | 90 | 64.3
| 100 | 43.5 |  | 100 | 67.5
| 120 | 48 |  | 120 | 73
| 140 | 52.5 |  | 140 | 77
| 160 | 57 |  | 160 | 81
| 180 | 61 |  | 180 | 85.5
| 200 | 65 |  | 200 | 90
| 225 | 70 |  | 225 | 95.5
| 250 | 75 |  | 250 | 101
| 275 | 80 |  | 275 | 104.5
| 300 | 85 |  | 300 | 108
| 400 | 105 |  | 400 | 127
| 500 | 124 |  | 500 | 143
| 750 | 170 |  | 750 | 177
| 1000 | 208 |  | 1000 | 208
| 1250 | 239 |  | 1250 | 239
| 1500 | 269 |  | 1500 | 269
| 1750 | 297 |  | 1750 | 297
| 2000 | 325 |  | 2000 | 325
| 2500 | 380 |  | 2500 | 380
| 3000 | 433 |  | 3000 | 433
| 4000 | 525 |  | 4000 | 525
| 5000 | 593 |  | 5000 | 593
HAZEN WILLIAMS FORMULA

## 5-Definitions
Definitions Sheet
PWD Water Service Line Sizing Model
Full-bath Group (Flush Tank) - 1 Tank Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Full-bath Group (Flushometer Valve)- 1 Flushometer Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Half-bath Group (Flush Tank)- 1 Tank Toilet and 1 Bathroom Sink
Bathtub / Shower Combination- This fixture has a bathtub as the basin base with a bath shower atop it and is located in PRIVATE space. This fixture can only use either the tub faucet OR the shower head. Not both at the same time.
Combination Fixture- This fixture combines the functions of a sink and a toilet into a single fixture and is located in PRIVATE space.
Water Closet (Tank Toilet)- This is a toilet that has a tank on the back that holds water. If there is no tank the fixture is called a Flushometer Valve toilet.
Water Closet (Flushometer Valve)- This type of toilet has no tank to store the water on the back. The water pipe comes directly out of the wall and fills the bowl.
Water Closet (Flushometer Tank)- This fixture combines a Flushometer Valve with a tank. The valve allows a certain amount of water to fill the tank quickly at a high rate.
Laundry Tub- A sink located in a laundry room or utility room.
Hose Bibs (ALL Public and Private Bibs)- An outside faucet.
Urinal (1" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 1" valve.
Urinal (3/4" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 3/4" valve.
Urinal (Flush Tank)- A bathroom urinal located in PUBLIC space with a tank.
Domestic Demand- The water used by the fixtures and the mechanical equipment excluding fire and irrigation only.
IPC- International Plumbing Code

## 6A-Appendix
Appendix1
PWD Water Service Line Sizing Model
References:
https://www.badgermeter.com/product-documentation/
Notes:
1All data provided as reference only. Values provided should reflect installation proposed for project.
2Engineer completing form to provide values cooresponding to meter model proposed for the development.
PWD Meter Flow Range by Size
Manufacterer Pressure Loss Data for Water Meters (For Reference Only)2

## 6B-Appendix
Appendix1
PWD Water Service Line Sizing Model
References:
https://sensus.com/products/?utility=water
https://www.badgermeter.com/product-documentation/
Notes:
1All data provided as reference only. Values provided should reflect installation proposed for project.
2Engineer completing form to provide values cooresponding to meter model proposed for the development.
Manufacterer Pressure Loss Data for Water Meters (For Reference Only)2

## 6C-Appendix
Appendix1
PWD Water Service Line Sizing Model
References:
https://www.watts.com/products/
Notes:
1All data provided as reference only. Values provided should reflect installation proposed for project.
2Engineer completing form to provide values cooresponding to backflow preventer proposed.
Manufacterer Pressure Loss Data for Backflow Prevention (For Reference Only)2